# Vending Machine Install Survey Checklist — Weight, Floor Load, Clearance, and Electrical

Cabinet weight reference, point load calculation, structural review trigger, and ADA verification

Use this checklist when surveying a placement on an elevated floor, mezzanine, or any structurally sensitive area. Full-size vending machines fully loaded routinely exceed 1,200-1,500 lb. The point load at each leveling foot can reach 250-300 psf — well above the live-load assumption for residential or light-office construction. Mark each item Verified, Reviewed with engineer, or Reject before install.

# 1. Cabinet weight reference (empty vs. fully loaded)

| Machine type | Empty (lb) | Fully loaded (lb) | Approx. point load per foot |
| --- | --- | --- | --- |
| Snack (spiral) | 650-750 | 1,000-1,200 | 250-300 lb |
| Beverage (can/bottle) | 700-900 | 1,200-1,500 | 300-375 lb |
| Combo (snack + beverage) | 750-900 | 1,200-1,500 | 300-375 lb |
| Fresh-food / refrigerated | 750-900 | 1,100-1,400 | 275-350 lb |
| Coffee (bean-to-cup) | 400-700 | 500-850 | 125-215 lb |
| Micro-market kiosk | 150-300 | 200-400 | 50-100 lb |

# 2. Floor live load — IBC and ASCE 7 reference

☐  IBC Table 1607.1 live load values verified for the placement floor: light office 50 psf, retail / mercantile 75-100 psf, light manufacturing 125 psf.

☐  Point-load calculation: total loaded weight ÷ 4 leveling feet ÷ (typical 4 in² contact area) = lb/ft² applied locally. Most full-size cabinets exceed 250 psf at the foot.

☐  Concentrated load review per IBC 1607.4 — vending machines commonly classify as a concentrated load and must be reviewed against the floor system's concentrated capacity.

☐  Elevated floors (mezzanine, upper-story over a finished space, post-tensioned slabs) reviewed by a licensed structural engineer with sign-off documented.

☐  Wood-framed floors: joist span, spacing, and grade reviewed; load-distribution plywood pad or steel plate specified if the engineer recommends.

# 3. Clearance, ventilation, and service

☐  Front swing clearance ≥ 36 inches with the cabinet door fully open for restock; verified against manufacturer cut sheet.

☐  Rear ventilation clearance ≥ 4 inches; some refrigerated units require 6 inches or a vent grille to a service chase.

☐  Side clearance ≥ 2 inches between machines and ≥ 6 inches to a wall for cable runs.

☐  Top clearance ≥ 4 inches from cabinet to ceiling, sprinkler head, or HVAC diffuser; sprinkler deflector clearance ≥ 18 inches per NFPA 13 Section 8.6.5.

# 4. Electrical baseline

☐  Dedicated 20A 120V circuit per NEC 210.23; verify against machine nameplate FLA.

☐  GFCI receptacle per NEC 210.8(B) for commercial kitchens, break rooms with sinks, and outdoor locations.

☐  Voltage drop ≤ 3% at running load per NEC 210.19(A) Informational Note 4.

☐  Receptacle configuration matches cordcap (NEMA 5-15R, 5-20R, 6-20R, or 6-30R as applicable).

# 5. Anchoring, tip resistance, and ADA

☐  Cabinet anti-tip device installed per manufacturer recommendation (typical: L-bracket or wall strap from cabinet top to wall stud).

☐  Outdoor or seismic placements anchored to slab with concrete anchors per manufacturer spec and ASCE 7 seismic / wind coefficients for the jurisdiction.

☐  ADA Section 305 clear floor space (30 × 48 inches) preserved at the machine face.

☐  ADA Section 308 reach range: highest operable part ≤ 48 inches AFF; lowest operable part ≥ 15 inches AFF.

☐  Cabinet leveled per manufacturer spec (≤ ¼ inch out of plumb) before final anchoring.

This checklist is informational and not engineering advice. Live-load classifications, concentrated-load reviews, and seismic anchoring should be performed by a licensed structural engineer per IBC, ASCE 7, and local jurisdiction. LetUsVending can connect you with operators who survey each location before placement — request a site survey to start.